## Main
City = | Tuscaloosa | State = | AL
Heating(outdoor) | tdb(99.6%) = | 20
(Indoor) | tdb = | 70
Cooling(outdoor) | tdb(0.4%) = | 96 | twb(0.4%) = | 76 | DR = | 20 | DT(htg.) | 50
(Indoor) | tdb = | 75 | twb = | 63 | DT(pm) = | 21 | T (mean) = | 86
| W (Outdoor) = | 0.014858 | W (Indoor)= | 0.0096236 | DW | 0.0052339 | CLTD(Cor) = | 4
| Elevation (ft) = | 200 | Latitude = | 32 |  |  | Zone 1 |  |  |  | Zone 2 |  |  |  | Zone 3 |  |  |  | Zone 4
[5 empty] | Area (ft2) | qc (am) | qc(pm) | qh | Area (ft2) | qc (am) | qc(pm) | qh | Area (ft2) | qc (am) | qc(pm) | qh | Area (ft2) | qc (am) | qc(pm) | qh
Solar | Shade Coeff. | SCL (am) | SCL (pm)
Windows (N) |  | 35 | 35 |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Windows (E) |  | 142 | 48 |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Windows (S) |  | 43 | 48 |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Windows (W) |  | 32 | 140 |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Other | [5 empty] | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Conduction | U (Btu/hr-ft2-F) | CLTD(am) | CLTD(pm) | DT | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2)
Windows (N) |  | 4 | 14 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Windows (E) |  | 4 | 14 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Windows (S) |  | 4 | 14 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Windows (W) |  | 4 | 14 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Conduction | U (Btu/hr-ft2-F) | CLTD(am) | CLTD(pm) | DT | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2)
Walls (N) |  | 10 | 25 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Walls (E) |  | 45 | 38 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Walls (S) |  | 6 | 39 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Walls (W) |  | 5 | 33 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Conduction | U (Btu/hr-ft2-F) | CLTD(am) | CLTD(pm) | DT | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2)
Doors (N) |  | 15 | 30 | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Doors (E) |  | 64 | 31 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Doors (S) |  | 17 | 43 | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Doors (W) |  | 13 | 59 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Other |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Roof/Ceiling | U (Btu/hr-ft2-F) | CLTD(am) | CLTD(pm) | DT | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2)
Type A |  | 15 | 52 | 50 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Type B |  |  |  | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Floor | U (Btu/hr-ft2-F) |  |  | DT(flr) | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2) |  |  |  | Area (ft2)
|  |  |  | 50 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Slab/Basement | Ins. Position | Insulation | UP | DT(slab) | Per. (ft.) |  |  |  | Per. (ft.) |  |  |  | Per. (ft.) |  |  |  | Per. (ft.)
| Vertical | R5 x 48 in | 0.54 | 50 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
Ventilation |  | DT(am) | DT(pm) | DT | cfm |  |  |  | cfm |  |  |  | cfm |  |  |  | cfm
Sensible | 1.1 | 16.85 | 21 | 50 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
HRU Eff. (sen.) = |  | DW | DW
Latent | 4840 | 0.0052339 | 0.0052339 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
HRU Eff. (lat.) = |  |  |  |  | People |  |  |  | People |  |  |  | People |  |  |  | People
People | Btu/person | CLF(am) | CLF(pm)
Sensible | 250 | 0.78 | 0.94 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Latent | 200 | 1 | 1 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Internal |  | CLF(am) | CLF(pm) |  | Watts |  |  |  | Watts |  |  |  | Watts |  |  |  | Watts
Sensible | 3.412 | 0.78 | 0.94 |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
[5 empty] | Btu/h |  |  |  | Btu/h |  |  |  | Btu/h |  |  |  | Btu/h
Latent |  | 1 | 1 |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
|  | CLF(am) | CLF(pm) | F(ballast) | Watts |  |  |  | Watts |  |  |  | Watts |  |  |  | Watts
Lighting | 3.412 | 0.88 | 0.96 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Net Sen.w/o duct | [5 empty] | 0 | 0 | 0 | w/o duct | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Ductwork |  | Insulation | Leakage |  | Location |  |  |  | Location |  |  |  | Location |  |  |  | Location
Sensible |  | R4 | Sealed |  | ConSpc | 0 | 0 | 0 | S&R-Ext | 0 | 0 | 0 | S&R-Ext | 0 | 0 | 0 | S&R-Ext | 0 | 0 | 0
Latent | [5 empty] | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0
Total Sensible | (MBtu/h) | Entire | Building | Totals |  |  | Zone 1 |  |  |  | Zone 2 |  |  |  | Zone 3 |  |  |  | Zone 4
Total Latent | (MBtu/h) | 0 | 0 |  | Sens. | 0 | 0 |  | Sens. | 0 | 0 |  | Sens. | 0 | 0 |  | Sens. | 0 | 0
Total Gain | (MBtu/h) | 0 | 0 |  | Lat. | 0 | 0 |  | Lat. | 0 | 0 |  | Lat. | 0 | 0 |  | Lat. | 0 | 0
| SHR | 0 | 0 |  | Tot. Gain | 0 | 0 |  | Tot. Gain | 0 | 0 |  | Tot. Gain | 0 | 0 |  | Tot. Gain | 0 | 0
Total Loss | (MBtu/h) | 0 | 0 |  | SHR | 0 | 0 |  | SHR | 0 | 0 |  | SHR | 0 | 0 |  | SHR | 0 | 0
|  | 0 | Net Loss | 0 | Tot. Loss | 0 | Net Loss | 0 | Tot. Loss | 0 | Net Loss | 0 | Tot. Loss | 0 | Net Loss | 0 | Tot. Loss | 0 | Net Loss | 0
Enter CLTDs directly from Tables. Program will correct for temperatures.
Heating & Cooling Load Calculation Form - CLTD/CLF/SCL Method
See other sheets for CLTD, CLF, SCL & U-values.
Input values in Go to Worksheets below for values that can be cut and pasted into Main Worksheet. Values in other cells are caculated - References: ASHRAE Handbook of Fundamentals, 1997 and ACCA Manual N.
Add Building Description Here
Yellow Cells

## Weather
A | B | C | D | E |  | F |  | G |  |  |  | H
Location | Lat. | Elev. | Heating | Cooling 1 |  | Evaporation2 |  | Dehumidification3 |  |  |  | DB
|  |  | -99.6% | -0.4% |  | -0.4% |  | -0.4% |  |  |  | Range
|  |  |  | DB | MWB | WB | MDB | DP | HR | DB | WB
City/State | °N | Ft. | °F | °F | °F | °F | °F | °F | Gr4 | °F | °F | °F
Albuquerque, NM | 35 | 5320 | 13 | 96 | 60 | 65 | 83 | 61 | 98 | 68 | 63 | 25
Atlanta, GA | 34 | 1033 | 18 | 93 | 75 | 77 | 88 | 74 | 133 | 82 | 76 | 17
Baltimore, MD | 39 | 154 | 11 | 93 | 75 | 78 | 88 | 75 | 132 | 83 | 77 | 19
Birmingham, AL | 34 | 630 | 18 | 94 | 75 | 78 | 89 | 75 | 135 | 83 | 77 | 19
Boise, ID | 44 | 2870 | 2 | 96 | 63 | 66 | 90 | 58 | 79 | 72 | 63 | 30
Boston, MA | 42 | 30 | 7 | 91 | 73 | 75 | 87 | 72 | 119 | 80 | 74 | 15
Brownsville, TX | 26 | 20 | 36 | 95 | 78 | 80 | 89 | 78 | 146 | 83 | 79 | 17
Chicago, IL | 42 | 673 | -6 | 91 | 74 | 77 | 88 | 74 | 130 | 84 | 77 | 20
Cleveland, OH | 41 | 804 | 1 | 89 | 73 | 76 | 85 | 73 | 125 | 82 | 75 | 19
Dallas, TX | 33 | 597 | 17 | 100 | 74 | 78 | 92 | 75 | 132 | 82 | 77 | 20
Denver, CO | 40 | 5330 | -3 | 93 | 60 | 65 | 81 | 60 | 96 | 69 | 63 | 27
Lake Charles, LA | 30 | 33 | 29 | 93 | 78 | 80 | 88 | 78 | 148 | 84 | 80 | 16
Los Angeles, CA | 34 | 105 | 43 | 85 | 64 | 70 | 78 | 67 | 99 | 75 | 70 | 11
Miami, FL | 26 | 13 | 46 | 91 | 77 | 80 | 87 | 78 | 144 | 83 | 79 | 11
Minneapolis, MN | 45 | 837 | -16 | 91 | 73 | 76 | 88 | 73 | 124 | 83 | 76 | 19
Nashville, TN | 36 | 590 | 10 | 94 | 76 | 78 | 89 | 75 | 134 | 83 | 77 | 19
Omaha, NE | 41 | 1332 | -8 | 95 | 75 | 78 | 90 | 75 | 136 | 85 | 77 | 20
Oklahoma City | 35 | 1300 | 9 | 99 | 74 | 77 | 91 | 73 | 129 | 83 | 76 | 21
Phoenix, AZ | 34 | 1089 | 34 | 110 | 70 | 76 | 97 | 71 | 118 | 82 | 74 | 23
Raleigh, NC | 36 | 440 | 16 | 93 | 76 | 78 | 88 | 75 | 134 | 82 | 77 | 19
Sacramento, CA | 39 | 23 | 31 | 100 | 69 | 72 | 96 | 62 | 84 | 82 | 69 | 33
St. Louis, MO | 39 | 564 | 2 | 95 | 76 | 79 | 90 | 76 | 138 | 85 | 78 | 18
Salt Lake, UT | 41 | 4230 | 6 | 96 | 62 | 66 | 85 | 60 | 92 | 73 | 64 | 28
Seattle, WA | 47 | 450 | 23 | 85 | 65 | 66 | 83 | 60 | 78 | 71 | 64 | 18
Tallahassee, FL | 30 | 69 | 25 | 95 | 77 | 80 | 89 | 77 | 142 | 83 | 79 | 19
Tuscaloosa, AL | 33 | 171 | 20 | 96 | 76 | 80 | 90 | 77 | 142 | 84 | 79 | 20
1This design conditions typically result in the highest sensible cooling load and highest total load when ventilation requirements and infiltration are low. 2These design conditions will result in higher total cooling loads when the ventilation air requirements and infiltration are high in humid and moderate climates. 3These design conditions typically result cooling loads with the lowest sensible heat ratio (SHRLoad). 4 Gr = Grains of moisture (7000 Grains = 1 lb)
The Table below provides only a few of the sites listed in electronic format in the 2005 ASHRAE Fundamentals Handbook. The 2001 version of the Handbook (Chapter 27) contains tablular climatic data for over 1200 locations in the USA and Canada and 1700 international locations.

## R-U
| hr-°F-ft2 |  | hr-°F-ft2 |  | hr-°F-ft2 |  | Out. Surface | Out. Finish | Insulation | Other | Other | Int. Finish | In. Surf.
Air (Heat Flow▲▼) | Btu | Insulation | Btu | Structural | Btu | R(Total)= | 0.25 | 0.45 | 9.3 |  |  | 0.45 | 0.68 | 11.13
Ext. Surface (7½ mph) | 0.25 | 3½ inch Fiberglass | 11 | 8 inch LW block | 2 | R(Total)= | 11.13 | hr-ft2-F/Btu
Ext. Surface (15 mph) | 0.17 | w/ 20% wood framing | 9.6 | with perlite cores | 5.5 | U (Overall)= | 0.089847 | Btu/hr-ft2-F
Inside Surface | 0.68 | 3½ inch Fiberglass | 13 | 12 inch LW block | 2.4
1 in. Vertical Air Gap | 0.8-1.6 | w/ 20% wood framing | 10.5 | with perlite cores | 7.2
4 in. Vertical Air Gap | 0.9-1.5 | 5½ inch Fiberglass | 19 | 12 inch HW block | 1.11 | R(Total)= | 13 | hr-ft2-F/Btu
1 in. Horizontal Air Gap | 0.8▲-1.7▼ | w/ 10% wood framing | 17.3 | Concrete | 0.14/in. | U (Overall)= | 0.076923 | Btu/hr-ft2-F
4 in. Horizontal Air Gap | 0.8▲-2.2▼ | w/ 20% wood framing | 15.2 | Softwood | 1.25/in.
|  | 7¼ inch Fiberglass | 25 | Hardwood | 0.9/in.
Exterior Materials |  | w/ 10% wood framing | 21 |  |  |  | % Total Area | Out. Surface | Out. Finish | Insulation | Wood | Other | Other | Int. Finish | In. Surface | R-Path Total
U-Values in Btu /hr-°F-ft2 |  |  |  | R-Values in hr-°F-ft2/Btu |  | R-Insul. Path = | 80 | 0.25 | 0.45 | 13 |  |  |  | 0.45 | 0.68 | 14.83
4 inch Face Brick | 0.45 | 9¼ inch Fiberglass | 30 | U-Values in Btu/hr-°F-ft2 |  | R-Wood Path = | 20 | 0.25 | 0.45 |  | 4.4 |  |  | 0.45 | 0.68 | 6.23
Steel siding | 0 | w/ 10% wood framing | 26 | Windows | R / U
Vinyl Siding (0.06 in.) | 0.06 | 11¼ inch Fiberglass | 38 | Sgl. Pane Alum. frame | 0.79/1.27 | U (Overall)= | 0.086047 | Btu/hr-ft2-F
1 inch Stucco | 0.21 | w/ 10% wood framing | 32.5 | Dbl. Pane Alum. frame | 1.20/0.83 | R(Total)= | 11.6215 | hr-ft2-F/Btu
3/4 inch Plywood | 0.93 | Cellulose | 3.7/in. | Dbl. Vinyl/Alum. frame | 1.75/0.57
1/2 inch Plywood | 0.62 | w/ 10% wood framing | 3.1/in. | Dbl. Wood/Vinyl frame | 1.82/0.55
5/8 inch Hardboard | 0.85 | w/ 20% wood framing | 2.7/in. | Triple Vinyl/Al. frame | 2.30/0.43
3/8 inch Hardboard | 0.5 | Panel-3½"beadbrd.+OSB | 12.8 | Doors
1/2 in. Veg. (Black) Board | 1.32 | Panel-3½"extr.poly+OSB | 17 | 1-¾ inch Solid Wood | 2.50/0.40 | R per Inch | Inches
Roof Stone/Slag | 0.1/in. | 1 inch Duct Liner/Wrap | 4 | with storm door | 3.80/0.26 | 1.25 | 3.5
Building Wrap, Felt | ~ 0 | 2 inch Duct Liner/Wrap | 8 | 1-¾ inch Panel | 1.85/0.54 | R(Total)= | 4.375 | hr-ft2-F/Btu
7/16" OSB | 0.5 | Expanded Polysty (beads) | 3.5/in. | with storm door | 2.80//0.36 | U (Overall)= | 0.22857 | Btu/hr-ft2-F
Interior |  | Extruded Polystyrene | 5.0/in. | 1-¾ inch Insul. Metal | 2.50/0.40
1/2 inch Gypsum Board | 0.45 | Polyisocyanurate | 6.0/in. | with storm door | 3.80/0.26
5/8 inch Gypsum Board | 0.56 | Polyurethane foam | 6.0/in. | 2-¼ inch Solid Wood | 3.7/0.27
1/2 inch Acoustical Tile | 1.79 |  |  | with storm door | 5.0/0.20
R-Value Calculator
R-to-U Inverter
U-Value Calculator for Wood Frame Walls
R-per-Inch to R-Value Calculator
Table 7.1 R-Values for Building Materials and Structural Units

## CLTD
All |  |  | Hr = 10 | Hr = 15
Directions |  |  | 4 | 14
Wall Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
1 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 18 | 30 | 17 | 30 | 16 | 30 | 15 | 30 | 14 | 29 | 14 | 29 | 14 | 29 | 14 | 29 | 13 | 28
E | 63 | 31 | 63 | 31 | 64 | 31 | 64 | 31 | 64 | 31 | 64 | 31 | 64 | 31 | 64 | 31 | 64 | 30
S | 12 | 31 | 13 | 35 | 15 | 39 | 17 | 43 | 18 | 46 | 21 | 50 | 23 | 53 | 25 | 56 | 28 | 59
W | 13 | 59 | 13 | 59 | 13 | 59 | 13 | 59 | 13 | 59 | 13 | 59 | 13 | 59 | 13 | 59 | 13 | 58
Wall Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
2 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 12 | 25 | 12 | 25 | 11 | 25 | 10 | 25 | 9 | 24 | 9 | 24 | 9 | 24 | 9 | 24 | 9 | 24
E | 42 | 38 | 43 | 38 | 44 | 38 | 45 | 38 | 46 | 38 | 46 | 38 | 47 | 38 | 48 | 38 | 49 | 38
S | 4 | 27 | 4 | 31 | 5 | 35 | 6 | 39 | 6 | 42 | 7 | 45 | 8 | 49 | 8 | 52 | 9 | 55
W | 5 | 33 | 5 | 33 | 5 | 33 | 5 | 33 | 5 | 33 | 5 | 33 | 6 | 33 | 6 | 33 | 6 | 32
Wall Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
5 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 7 | 19 | 7 | 19 | 7 | 18 | 7 | 18 | 6 | 17 | 6 | 17 | 6 | 17 | 6 | 17 | 6 | 17
E | 22 | 37 | 23 | 37 | 24 | 37 | 25 | 38 | 25 | 38 | 25 | 38 | 27 | 39 | 27 | 39 | 28 | 39
S | 3 | 18 | 3 | 20 | 4 | 23 | 4 | 25 | 4 | 27 | 4 | 29 | 5 | 32 | 5 | 34 | 6 | 37
W | 4 | 20 | 4 | 20 | 5 | 20 | 5 | 20 | 5 | 20 | 5 | 20 | 6 | 20 | 6 | 20 | 6 | 20
Wall Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
6 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 8 | 17 | 8 | 17 | 8 | 17 | 8 | 17 | 7 | 16 | 7 | 16 | 7 | 16 | 7 | 16 | 7 | 16
E | 22 | 34 | 23 | 34 | 24 | 35 | 25 | 35 | 25 | 35 | 28 | 35 | 31 | 36 | 29 | 36 | 27 | 36
S | 4 | 16 | 4 | 18 | 5 | 21 | 5 | 23 | 5 | 25 | 6 | 27 | 7 | 30 | 7 | 32 | 8 | 34
W | 7 | 20 | 7 | 20 | 7 | 20 | 7 | 20 | 7 | 20 | 7 | 20 | 8 | 20 | 8 | 20 | 8 | 20
Wall Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
10 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 8 | 14 | 8 | 14 | 7 | 13 | 6 | 13 | 5 | 12 | 5 | 12 | 6 | 12 | 6 | 12 | 6 | 12
E | 15 | 30 | 15 | 31 | 15 | 33 | 15 | 34 | 14 | 35 | 14 | 35 | 15 | 36 | 15 | 36 | 16 | 36
S | 5 | 12 | 5 | 13 | 5 | 15 | 5 | 17 | 4 | 18 | 4 | 19 | 5 | 21 | 5 | 22 | 5 | 24
W | 11 | 15 | 10 | 15 | 9 | 14 | 8 | 14 | 7 | 13 | 7 | 13 | 8 | 13 | 8 | 13 | 8 | 13
Wall Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
16 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 8 | 11 | 8 | 11 | 8 | 11 | 8 | 11 | 7 | 10 | 7 | 10 | 8 | 10 | 8 | 10 | 8 | 10
E | 11 | 26 | 11 | 26 | 12 | 27 | 12 | 28 | 12 | 28 | 12 | 28 | 13 | 29 | 13 | 29 | 14 | 29
S | 6 | 8 | 6 | 9 | 7 | 10 | 7 | 12 | 7 | 12 | 8 | 13 | 10 | 15 | 10 | 16 | 10 | 17
W | 12 | 11 | 12 | 11 | 13 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 14 | 12 | 14 | 12 | 14 | 12
Roof Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
| Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | 33 Deg. N | 33 Deg. N | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
1 | 44 | 92 | 45 | 92 | 45 | 91 | 45 | 91 | 45 | 90 | 45 | 89 | 45 | 87 | 45 | 85 | 44 | 83
2 | 30 | 90 | 31 | 90 | 31 | 89 | 32 | 89 | 32 | 88 | 32 | 87 | 32 | 85 | 32 | 84 | 32 | 82
3 | 22 | 74 | 22 | 74 | 23 | 74 | 24 | 74 | 24 | 73 | 24 | 72 | 24 | 71 | 24 | 70 | 24 | 68
4 | 5 | 67 | 6 | 67 | 6 | 67 | 7 | 67 | 7 | 66 | 7 | 65 | 8 | 64 | 8 | 63 | 8 | 62
5 | 10 | 61 | 11 | 61 | 11 | 61 | 12 | 61 | 12 | 61 | 12 | 60 | 13 | 59 | 13 | 58 | 13 | 57
8 | 14 | 59 | 15 | 57 | 15 | 54 | 15 | 52 | 15 | 49 | 15 | 49 | 16 | 48 | 16 | 47 | 16 | 46
9 | 5 | 46 | 6 | 46 | 6 | 46 | 7 | 46 | 7 | 46 | 7 | 46 | 8 | 45 | 8 | 44 | 8 | 43
10 | 8 | 37 | 9 | 43 | 9 | 48 | 9 | 43 | 9 | 38 | 9 | 38 | 10 | 37 | 10 | 37 | 10 | 36
13 | 16 | 38 | 17 | 38 | 17 | 38 | 17 | 38 | 17 | 38 | 17 | 38 | 18 | 38 | 18 | 38 | 18 | 37
14 | 19 | 36 | 20 | 36 | 20 | 36 | 20 | 36 | 20 | 36 | 20 | 36 | 20 | 36 | 20 | 36 | 20 | 35
Wall Cooling Load Temperature Differences (F) (Wall Type 1 Suggested for Opague Doors)
Roof Cooling Load Temperature Differences (F)
Window and Glass Door Cooling Load Temperature Differences (F)

## SC-SCL
|  | Glass | Alum | Wood | Vinyl |  |  | BLINDS | Med. Blind | Lt. Blind | Med. Blind | Lt. Blind | Dark Roller | White Roller
Glass Type | Gap | Only | Frame | Frame | Frame |  | # of Panes | Win. Tint | at 45° | at 45° | Closed | Closed | Closed | Closed
Sgl.-⅛"Clear | ─ | 1 | 0.86 | 0.72 | 0.72 |  | Single | Clear | 0.74 | 0.67 | 0.63 | 0.58 | 0.81 | 0.39
Sgl.-¼"Acryl | ─ | 0.93 | 0.82 | 0.69 | 0.69 |  | Double | Clear | 0.62 | 0.58 | 0.63 | 0.58 | 0.71 | 0.35
Dbl.-⅛"Clear | ¼" air | 0.87 | 0.76 | 0.63 | 0.63 |  | Double | e=0.2 | 0.39 | 0.36 | - | - | 0.4 | 0.22
Dbl.-⅛"Clear | ½"argon | 0.87 | 0.76 | 0.63 | 0.63 |  |  | DRAPES | Drape Color / Weave
Dbl-⅛"ε=0.2 | ¼" air | 0.7 | 0.66 | 0.55 | 0.55 |  | # of Panes | Win. Tint | Lt./Open | Med./Open | Dk./Open | Lt./Closed | Med./Closed | Dk./Closed
Dbl-⅛"ε=0.2 | ½"argon | 0.7 | 0.66 | 0.55 | 0.55 |  | Single | Clear | 0.69 | 0.74 | 0.82 | 0.69 | 0.59 | 0.39
Trpl-⅛"Clear | ¼" air | 0.71 | 0.68 | 0.59 | 0.59 |  | Double | Clear | 0.63 | 0.65 | 0.71 | 0.63 | 0.53 | 0.35
Trpl-⅛"Clear | ½"argon | 0.71 | 0.68 | 0.59 | 0.59 |  | Double | e=0.2 | 0.36 | 0.37 | 0.37 | 0.36 | 0.32 | 0.22
Zone Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
A | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 38 | 38 | 37 | 38 | 36 | 37 | 36 | 36 | 37 | 36 | 36 | 36 | 35 | 36 | 35 | 36 | 34 | 35
E | 154 | 40 | 154 | 40 | 155 | 40 | 155 | 40 | 155 | 39 | 155 | 39 | 154 | 39 | 153 | 39 | 153 | 38
S | 35 | 37 | 39 | 41 | 44 | 45 | 49 | 48 | 53 | 52 | 63 | 61 | 72 | 70 | 81 | 79 | 90 | 88
W | 35 | 160 | 35 | 160 | 35 | 160 | 35 | 160 | 35 | 159 | 35 | 159 | 35 | 159 | 35 | 158 | 34 | 156
Zone Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
B | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 35 | 37 | 35 | 36 | 34 | 35 | 35 | 35 | 36 | 35 | 35 | 35 | 34 | 35 | 33 | 35 | 32 | 34
E | 141 | 48 | 142 | 48 | 142 | 48 | 142 | 48 | 143 | 48 | 143 | 48 | 143 | 48 | 143 | 48 | 143 | 47
S | 31 | 36 | 35 | 40 | 39 | 44 | 43 | 48 | 47 | 52 | 55 | 67 | 63 | 81 | 70 | 95 | 78 | 109
W | 32 | 141 | 32 | 141 | 32 | 140 | 32 | 140 | 32 | 140 | 32 | 140 | 32 | 139 | 32 | 138 | 31 | 137
Zone Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
C | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 32 | 34 | 32 | 34 | 32 | 33 | 32 | 33 | 31 | 32 | 31 | 32 | 31 | 32 | 31 | 31 | 30 | 31
E | 123 | 47 | 123 | 47 | 124 | 47 | 124 | 47 | 124 | 47 | 124 | 47 | 124 | 47 | 124 | 47 | 124 | 47
S | 29 | 32 | 33 | 36 | 37 | 39 | 41 | 42 | 45 | 45 | 53 | 53 | 60 | 61 | 67 | 68 | 75 | 76
W | 34 | 132 | 34 | 132 | 34 | 132 | 34 | 132 | 34 | 132 | 34 | 131 | 34 | 131 | 34 | 131 | 33 | 130
Zone Type | 24 Deg. N | 24 Deg. N | 27 Deg. N | 27 Deg. N | 30 Deg. N | 30 Deg. N | 33 Deg. N | 33 Deg. N | 36 Deg. N | 36 Deg. N | 39 Deg. N | 39 Deg. N | 42 Deg. N | 42 Deg. N | 45 Deg. N | 45 Deg. N | 48 Deg. N | 48 Deg. N
D | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15
N | 29 | 33 | 29 | 33 | 28 | 32 | 28 | 32 | 27 | 31 | 27 | 31 | 27 | 31 | 27 | 31 | 27 | 30
E | 108 | 52 | 108 | 52 | 109 | 53 | 109 | 53 | 110 | 53 | 110 | 53 | 111 | 53 | 111 | 53 | 111 | 53
S | 25 | 30 | 28 | 33 | 32 | 37 | 35 | 40 | 39 | 43 | 45 | 50 | 52 | 58 | 58 | 65 | 64 | 72
W | 32 | 112 | 32 | 112 | 33 | 112 | 33 | 112 | 33 | 112 | 33 | 111 | 33 | 111 | 33 | 110 | 33 | 110
SCL - Solar Cooling Loads - (Btu/hr-ft2) Note: To determine Zone Type, go to Wall Type Worksheet
Shade Coefficients (SC) for Unshaded Windows
SCs for Windows with Interior Shades Coefficients

## HeatGain
|  | Sensible | Latent | Total
Activity | Level | Heat Gain | Heat Gain | Heat Gain
Seated | at Rest | 245 | 105 | 350
Seated | Light work | 245 | 155 | 400
Office work | Moderate | 250 | 200 | 450
Standing | Walking | 250 | 250 | 500
Light | Bench work | 275 | 475 | 750
Nightclub | Dancing | 305 | 545 | 850
Heavy | Work | 580 | 870 | 1450
Heat Gain From Occupants - Btu/hr person
Heat Gain From Lighting - Watts (For incandescent fixtures, Bulb Watts = Fixture Watts)
Heat Gain From Office Equipment

## CLF
| Zone | Type A | Zone | Type B | Zone | Type C | Zone | Type D
Occupancy | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Occupancy
8 hrs/day | 0.93 | 0.97 | 0.87 | 0.95 | 0.82 | 0.9 | 0.74 | 0.85 | 8 hrs/day
12 hrs/day | 0.94 | 0.98 | 0.88 | 0.96 | 0.84 | 0.92 | 0.77 | 0.87 | 12 hrs/day
16 hrs/day | 0.95 | 0.98 | 0.9 | 0.97 | 0.97 | 0.93 | 0.81 | 0.89 | 16 hrs/day
| Zone | Type A | Zone | Type B | Zone | Type C | Zone | Type D
Occupancy | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Occupancy
8 hrs/day | 0.9 | 0.98 | 0.78 | 0.94 | 0.72 | 0.89 | 0.71 | 0.85 | 8 hrs/day
12 hrs/day | 0.9 | 0.98 | 0.78 | 0.94 | 0.73 | 0.89 | 0.73 | 0.87 | 12 hrs/day
16 hrs/day | 0.91 | 0.98 | 0.8 | 0.94 | 0.76 | 0.91 | 0.78 | 0.89 | 16 hrs/day
| Zone | Type A | Zone | Type B | Zone | Type C | Zone | Type D
Occupancy | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Hr = 10 | Hr = 15 | Occupancy
8 hrs/day | 0.86 | 0.97 | 0.68 | 0.91 | 0.6 | 0.82 | 0.6 | 0.77 | 8 hrs/day
12 hrs/day | 0.86 | 0.97 | 0.69 | 0.92 | 0.6 | 0.82 | 0.62 | 0.82 | 12 hrs/day
16 hrs/day | 0.87 | 0.97 | 0.72 | 0.92 | 0.66 | 0.88 | 0.68 | 0.85 | 16 hrs/day
Cooling Load Factors - Lights (Lights Turned on between 7 & 8 am)
Cooling Load Factors - People & Unhooded Equip. (Occupancy Begins between 7 & 8 am)
Cooling Load Factors - Hooded Equipment (Occupancy Begins between 7 & 8 am)
Note: To Determine Zone Type, Go To Wall & Roof Types Worksheet

## VentAir
ASHRAE 62.1-2004 | Ventilation Rate | Procedure |  | Input Req'd | Output
Zone Description | Zone # | Rp | # of People | Rp*people | Ra | A (ft2) | Ra*Area | Vp | Zp
Office | 1 | 5 | 1 | 5 | 0.06 | 154 | 9.24 | 154 | 0.092468
Reception | 2 | 5 | 6 | 30 | 0.06 | 176 | 10.56 | 176 | 0.23045
Workroom | 3 | 5 | 2 | 10 | 0.06 | 138 | 8.28 | 138 | 0.13246
Conference | 4 | 5 | 12 | 60 | 0.06 | 390 | 23.4 | 390 | 0.21385
Office | 5 | 5 | 1 | 5 | 0.06 | 110 | 6.6 | 110 | 0.10545
Break | 6 | 5 | 5 | 25 | 0.06 | 110 | 6.6 | 110 | 0.28727
Office | 7 | 5 | 1 | 5 | 0.06 | 121 | 7.26 | 121 | 0.10132
8
9
10
Totals |  |  | 28 | 140 |  |  | 71.94
Max occupants | 12
Diversity | 0.42857
Ez | 1
Vou | 131.94
Estimated Vp/A | 1 | cfm/ft2
Ev | 0.8
Vo | 164.925 | cfm
Occupancy Category | People Factor |  | Area factor |  |  | Default Values
| cfm/person | Lps/Person | cfm/ft2 | Lps/m2 | Peo./1000 ft2 | cfm/person | Lps/person
| Rp (IP Units) | Rp (SI Units) | Ra (IP Units) | Ra (SI Units) | (Peo./100 m2)
Education
Day Care | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6
Classroom (age 5-8) | 10 | 5 | 0.12 | 0.6 | 25 | 15 | 7.4
Classroom (age 9+) | 10 | 5 | 0.12 | 0.6 | 35 | 13 | 6.7
Lecture Classroom | 7.5 | 3.8 | 0.06 | 0.3 | 65 | 8 | 4.3
Food & Beverage
Restaurant Dining | 7.5 | 3.8 | 0.18 | 0.9 | 70 | 10 | 5.1
Cafeteria/fast food | 7.5 | 3.8 | 0.18 | 0.9 | 100 | 9 | 4.7
Hotels, Dorms
Bed/Living rooms | 5 | 2.5 | 0.06 | 0.3 | 10 | 11 | 5.5
Lobbies/pre-function | 5 | 2.5 | 0.06 | 0.3 | 20 | 8 | 4
Assembly | 5 | 2.5 | 0.06 | 0.3 | 120 | 6 | 2.8
Office Buildings
Office space | 5 | 2.5 | 0.06 | 0.3 | 5 | 17 | 8.5
Reception area | 5 | 2.5 | 0.06 | 0.3 | 30 | 7 | 3.5
Telephone/data entry | 5 | 2.5 | 0.06 | 0.3 | 60 | 6 | 3
Public Assembly
Conference | 5 | 2.5 | 0.06 | 0.3 | 50 | 6 | 3.1
Auditorium | 5 | 2.5 | 0.06 | 0.3 | 150 | 5 | 2.7
Library | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5
Museum | 7.5 | 3.8 | 0.06 | 0.3 | 40 | 9 | 4.6
Retail
Sales | 7.5 | 3.8 | 0.12 | 0.6 | 15 | 16 | 7.8
Mall - common area | 7.5 | 3.8 | 0.06 | 0.3 | 40 | 9 | 4.6
Supermarket | 7.5 | 3.8 | 0.06 | 0.3 | 8 | 15 | 7.6
Sports
Gym, playing areas | - | - | 0.3 | 1.5 | 30 | - | -
Spectator areas | 7.5 | 3.8 | 0.06 | 0.3 | 150 | 8 | 4
Aerobics room | 20 | 10 | 0.06 | 0.3 | 40 | 22 | 10.8
Dance floor | 20 | 10 | 0.06 | 0.3 | 100 | 21 | 10.3
Game arcade | 7.5 | 3.8 | 0.18 | 0.9 | 20 | 17 | 8.3
Zone Description | Zone # | Rp | # of People | Rp*people | Ra | A (ft2) | Ra*Area | Vp | Zp
Office | 1 | 5 | 1 | 5 | 0.06 | 100 | 6 | 100 | 0.11
Office | 2 | 5 | 1 | 5 | 0.06 | 92 | 5.52 | 92 | 0.11435
Office | 3 | 5 | 1 | 5 | 0.06 | 92 | 5.52 | 92 | 0.11435
Office | 4 | 5 | 1 | 5 | 0.06 | 92 | 5.52 | 92 | 0.11435
Office | 5 | 5 | 1 | 5 | 0.06 | 149.5 | 8.97 | 149.5 | 0.093445
Office | 6 | 5 | 1 | 5 | 0.06 | 100 | 6 | 100 | 0.11
Office | 7 | 5 | 1 | 5 | 0.06 | 110 | 6.6 | 110 | 0.10545
Conference | 8 | 5 | 8 | 40 | 0.06 | 312 | 18.72 | 312 | 0.18821
9
10
Totals |  |  | 15 | 75 |  |  | 44.13
Max occupants | 8
Diversity2 | 0.53333
VentEff | 1
Vou | 84.13
Estimated Vp/A | 1 | cfm/ft2
Ev | 0.9
Vo | 93.4778 | cfm

## Slab
Slab Insulation |  | Unheated Slabs |  |  |  |  | Heated Slabs
Insulation | hr-°F-ft2 | Insulation Depth or Width (in.) |  |  |  |  | Insulation Depth or Width (in.)
Position* | Btu | 0 | 12 | 24 | 36 | 48 | 0 | 12 | 24 | 36 | 48
Horizontal | RIns=5 | 0.73 | 0.72 | 0.7 | 0.68 | 0.67 | 1.35 | 1.31 | 1.28 | 1.24 | 1.2
| RIns =10 | 0.73 | 0.71 | 0.7 | 0.66 | 0.64 | 1.35 | 1.3 | 1.26 | 1.2 | 1.13
Vertical | RIns=5 | 0.73 | 0.61 | 0.58 | 0.56 | 0.54 | 1.35 | 1.06 | 0.99 | 0.95 | 0.91
| RIns =10 | 0.73 | 0.58 | 0.54 | 0.51 | 0.48 | 1.35 | 1 | 0.9 | 0.84 | 0.78
Horz.+ Vert. | For RIns=5, | Insulation Depth or Width (in.) 24: For RIns=10,; Insulation Depth or Width (in.) 0: For RIns=5,; Insulation Depth or Width (in.) 36: For RIns=10,
(Fully Insul.) | F=0.46 | Insulation Depth or Width (in.) 24: F=0.36; Insulation Depth or Width (in.) 0: F=0.74; Insulation Depth or Width (in.) 36: F=0.55
Crawl Space or |  | Insulation Depth or Width (in.) 12: Fcsb (Btu/hr-ft-°F)
Basement Heights |  | Insulation Depth or Width (in.) 12: {qcsb=Fcsb×PBldg(ft)×[ti-to](°F)}
Lag | Lbg | Insulation Depth or Width (in.) 0: Lcsb; Insulation Depth or Width (in.) 12: RIns.= 0; Insulation Depth or Width (in.) 24: RIns.= 4; Insulation Depth or Width (in.) 36: RIns.= 8; Insulation Depth or Width (in.) 48: RIns.= 12
(ft.) | (ft.) | Insulation Depth or Width (in.) 0: (ft.); Insulation Depth or Width (in.) 12: hr-ft2-°F/Btu; Insulation Depth or Width (in.) 24: hr-ft2-°F/Btu; Insulation Depth or Width (in.) 36: hr-ft2-°F/Btu; Insulation Depth or Width (in.) 48: hr-ft2-°F/Btu
| 1 | Insulation Depth or Width (in.) 0: 2; Insulation Depth or Width (in.) 12: 1.13; Insulation Depth or Width (in.) 24: 0.39; Insulation Depth or Width (in.) 36: 0.24; Insulation Depth or Width (in.) 48: 0.17
1 | 4 | Insulation Depth or Width (in.) 0: 5; Insulation Depth or Width (in.) 12: 4.42; Insulation Depth or Width (in.) 24: 2.08; Insulation Depth or Width (in.) 36: 1.41; Insulation Depth or Width (in.) 48: 1.07
| 7 | Insulation Depth or Width (in.) 0: 8; Insulation Depth or Width (in.) 12: 9; Insulation Depth or Width (in.) 24: 4.71; Insulation Depth or Width (in.) 36: 3.34; Insulation Depth or Width (in.) 48: 2.62
| 1 | Insulation Depth or Width (in.) 0: 5; Insulation Depth or Width (in.) 12: 2.95; Insulation Depth or Width (in.) 24: 0.92; Insulation Depth or Width (in.) 36: 0.55; Insulation Depth or Width (in.) 48: 0.4
4 | 3 | Insulation Depth or Width (in.) 0: 7; Insulation Depth or Width (in.) 12: 4.96; Insulation Depth or Width (in.) 24: 1.91; Insulation Depth or Width (in.) 36: 1.22; Insulation Depth or Width (in.) 48: 0.9
| 5 | Insulation Depth or Width (in.) 0: 9; Insulation Depth or Width (in.) 12: 7.62; Insulation Depth or Width (in.) 24: 3.41; Insulation Depth or Width (in.) 36: 2.3; Insulation Depth or Width (in.) 48: 1.75
| 1 | Insulation Depth or Width (in.) 0: 8; Insulation Depth or Width (in.) 12: 4.76; Insulation Depth or Width (in.) 24: 1.45; Insulation Depth or Width (in.) 36: 0.86; Insulation Depth or Width (in.) 48: 0.61
7 | 2 | Insulation Depth or Width (in.) 0: 9; Insulation Depth or Width (in.) 12: 5.66; Insulation Depth or Width (in.) 24: 1.87; Insulation Depth or Width (in.) 36: 1.14; Insulation Depth or Width (in.) 48: 0.82
| 3 | Insulation Depth or Width (in.) 0: 10; Insulation Depth or Width (in.) 12: 6.78; Insulation Depth or Width (in.) 24: 2.44; Insulation Depth or Width (in.) 36: 1.54; Insulation Depth or Width (in.) 48: 1.12
Table 7.5 Slab Perimeter Heat Transmission Coefficients (Fs) in Btu/hr-ft-°F
Table 7.6 Crawl Space and Basement Heat Transmission Coefficients (Fcsb) in Btu/hr-ft-°F